頁次：1/1

摘要

本次任務主要是兌現2004年6月27日由公司第二次組團前往查京恩加美納爭取查德礦區石油探採權，及向查德政府官員簡報所擬『查德能源及電力發展的短期改善查得電力系統計畫』，展現中油公司協助『查德能源及電力發展計畫』之誠意，提供三台MBH柴油發電機組安裝監工、測試及驗收等技術支援工作。

本次工作團隊成員共三人，在黃建輝專案帶領下首先拜會(Societe Tchadienne d’Eau et d’Electricte,以下簡稱STEE)管理階層及電廠重要幹部和工作伙伴，熟悉工作環境與STEE電廠機組運轉狀況、瞭解任務性質與MBH機組安裝進度及機組測試所需之各項資料後展開為期約三個月的機組安裝測試驗收工作。

由於查德首都恩加美納只有一座電廠，廠內發電機組共16台全部都是柴油發電機，只有7台可以運轉，總裝置容量33MW只能發電約7MW供電能力相當薄弱經常實施限電，由於黑人操作習性不佳，加上維修經費不足，得過且過心態致大部分機組故障停機。查京只有總統府、機場、重要軍事設施與行政機關全日供電外，其餘單位與百姓均需輪流供電，每日供電時間約8小時其餘時間需仰賴用戶自備發電機或過著無電的生活，所以政府與人民對於MBH發電機組完工運轉(可供電約16MW)寄予厚望。本次工作團隊成員在此任務中充分發揮各人所長，從工程裝機、測試、驗收中以中油經驗提出嚴謹之品質要求和測試驗收標準，給予承攬本案之比利時承包商(IMM公司)相當大之壓力，使之不得不在品質安全性能等方面認真考量。另一方面也教育查德人民有權要求承攬商依照業主需求改善不合理、不安全、不符規格之設備或施工方法，對於自己應有的權利切莫任其睡著。

此次順利完成3部MBH機組試車驗收工作，加入查德電廠系統運轉已大幅增加供電能力，大大改善查京百姓用電之不便性，獲得相當讚許與肯定。於3月9日晚上自查京搭機返國，在3月11日返抵國門後，完成整個行程，圓滿達成任務。

一、目的

本次任務主要是中油公司爭取查德礦區石油探採權之鋪路工作，兌現向查德政府官員簡報所擬『查德能源及電力發展的短期改善查得電力系統計畫』，展現中油公司協助『查德能源及電力發展計畫』之誠意，提供三台MBH柴油發電機組安裝監工、測試及驗收等技術支援工作，以利中油公司對於查德油田礦區探採權能順利取得。

工作內容著重於電廠發電機安裝進度督導、測試及驗收等工作，除此之外，並就現存查德電力系統之瓶頸提出改善建議，另一方面也落實國民外交。首先與電廠重要幹部和工作伙伴溝通任務認知，熟悉工作環境與STEE電廠機組運轉狀況、瞭解MBH機組安裝進度及機組測試所需之各項資料，隨即展開為期約三個月的機組安裝測試驗收工作，期間也提出中油在建廠、操作運轉、維護保養等方面經驗供查德電廠參考，最後順利完成三部MBH柴油發電機組併聯發電，大大改善查德首都恩加美納地區輪流停電之惡夢。

二、過程

1.電廠現況

查京電力系統最大之問題在於發電量不足以供應全市所需，由於長期被法國殖民統治民生經濟無法發展，電力設備都還沿用三十幾年前系統，在獨立後仍無法擺脫被統治陰影再加上國內內戰頻繁無力發展建設與設備更新，所以電廠內大部分發電機組機齡高、運轉效率低加上操作員心態不求甚解又沒足夠經費做維護保養，導致大多數發電機組不是長期報廢停擺就是待料維修，總共16台能用的約7台左右，此行統計恩加美納地區用電負載需求約21MW而電廠能供應之電力約7～13MW，經常需要實施限電或輪流供電措施，近年來查國蘊藏之石油為外商陸續進駐主因，商機發展蓬勃，用電量持續成長，電廠供電能力之提升成為查德政府所關切之問題，也期望此次施工品質能在我方技術監督下有所提高，避免像NO.7發電機因施工不良導致完工不久後(約三個月)，新機組發生火災燒毀。因此對於MBH發電機組安裝與運轉寄予高度期望。

除了電廠發電容量不足外，恩加美納市區輸配電線路老舊，多處變電所還停留在三十幾年前之DS(Disconnect Switch)+Fuse操作，保護設備非常簡陋，甚至2005.02.09曾發生某處地下電纜故障導致全電廠發電機跳脫事故，首都恩加美納全部停電，又因配電方式採直埋式地下電纜佈設，簡陋的儀器將故障點查修花費3天才找出來，效率非常低。

2.電廠機組概述

由表一為全電廠可運轉機組數量及供電能力，舊機組機齡相當高，此次安裝之MBH機組是將來之主力。

表一 STEE電廠2004年底總供電能力

| 發電機組廠牌 | 機組 編號 | 尖峰發電能力 （MW） | 使用燃料 | 完工商轉年份 |
| --- | --- | --- | --- | --- |
| SEMT Pielstick | GE4 | 3.5 | 輕柴油 | 1972 |
| SEMT Pielstick | GE5 | 3.0 | 輕柴油 | 1965 |
| SEMT Pielstick | GE6 | 3.5 | 輕柴油 | 1985 |
| DEUTZ | GE8 | 1.5 | 輕柴油 | 1974 |
| DEUTZ | GE9 | 1.5 | 輕柴油 | 1976 |
| MBH | MBH1 | 4.2 | 重油 | 2004 |
| MBH | MBH2 | 4.2 | 重油 | 2004 |
| MBH | MBH3 | 4.2 | 重油 | 2004 |
| CATERPILLAR | CAT1 | 1.25 | 輕柴油 | 2004 |
| CATERPILLAR | CAT2 | 1.25 | 輕柴油 | 2004 |
| CATERPILLAR | CAT3 | 1.25 | 輕柴油 | 2004 |
| CATERPILLAR | CAT4 | 1.25 | 輕柴油 | 2004 |

在第一組機組試車或運轉期間，第二、三組機組尚施工中之安全防護，包含高壓盤、變壓器高低壓側與高壓盤間帶電體感電防止，焊接中管線可能因燃料油蝶閥洩漏或誤操作引火災等細節問題都已點出並要求確實做好安全防護。

查京恩加美納地區之既有配電系統共7回路，沒清理保養計畫，天花板是否防火功能，將來發生電氣短路故障將引起火災甚至影響整個恩加美納大停電。已通知改善。

3.發電機組安裝測試紀要

STEE以往都以Turn Key方式由承商建造後接收運轉，在保固期限內發生故障則由原廠派員與提供材料修復，其間所延宕或停機造成之限電責任由STEE自負。此次MBH機組使用零件較以往舊機組不同，要求在施工、建造、試車期間請STEE公司派員參與以落實機組接收和操作。以下是部分工作紀要：

- 93.12.28～94.01.07量變壓器絕緣、線路絕緣、布氏電驛測試，但沒做Hi-Pot已要求IMM但沒反應也沒做就送電(已告知STEE但沒處理)，高壓盤BUS、PT、CT、CB等只有用Megger量一量就送電，保護電驛沒有送電壓/電流模擬確認跳脫是否正常，目前Incoming開關投入送電到Bus Bar及輔助變壓器(15KV/400V)一回路，(3 phase 400/230V Y connection)室內外照明、插座、動力有電。

- 94.01.07變壓器送電供應輔機測試、Check控制盤燈號、指示值、量相序均正常。

- 接著陸續測試冷卻水泵、風扇(10台/Gen)之運轉效果與效能、有查洩漏目前正常，但管路焊口沒有探漏(NDT)，已要求IMM但沒反應也沒做(已告知STEE但沒處理)。其中一個風扇葉片、散熱片因放置機場過久而腐蝕，IMM處理中(待料停轉不影響試車工作)。

- 輔助油泵打油循環、滑油淨油機、過濾器、冷卻器等測試，壓力、溫度正常。管路沒Flash也沒酸洗只有靠清洗或更換既有Filter強迫洗管，IMM利用當地廉價之黑人勞工清洗、更換濾網。

- 空氣壓縮機單機測試壓力、溫度正常。

- 柴油系統：柴油泵打油循環、柴油淨油機、過濾器等壓力、溫度正常。管路沒Flash也沒酸洗只有靠清洗或更換既有Filter強迫洗管，IMM也是利用當地廉價之黑人勞工清洗、更換濾網。

- 電氣控制系統回路測試、儀器回路沒有單點校正與測試，已通知改善。

- 發電機要求做開路試驗、短路試驗，但IMM不願意，同步併聯前要求在高壓側核對相位是否正確，IMM說只有在低壓側量過無誤即可，我質疑其安全性堪慮，IMM基本上同意我的看法但以前都是這麼做，而且查德恩加美納這種隨時可停電的地區是可以接受這種作法的，而且目前沒儀器設備所以不做，該部分已要求釐清責任歸屬。

- 引擎與發電機聯軸器對心、曲軸軸承間隙檢查、燃料系統調整噴油嘴間距、空氣壓力調整。

- 恩加美納地區電壓變動非常大，沒停電的情況下居然電壓從90V～290V都曾經發生過，大使館、農技團、醫療團電子類電器經常燒壞。

- 柴油引擎振動大引起滑油、柴油管線洩漏，儀器因振動大可能而故障造成停機。

- 要求承商IMM公司製作操作手冊供操作員閱讀與演練，內容中需清楚的教導正常/緊急開、停機步驟，各項安全連鎖裝置和設定值(包含保護電驛，如過電流、差動、失磁、低頻...等)、各種儀器顯示正常操作值及異常時之警報值(alarm)、故障排除方法、輔機(auxiliary equipment)啟動停止方法步驟。

- 發電系統流程圖、電氣圖有許多部分與設計不符，若配合試車階段需修改，則需經STEE同意並適時更新最新版圖面。

- 燃料油槽容量過小，當所有機組發電時可能因燃料供應短缺(斷料)而停機。

- 廠內所有發電機因分散各地，欠缺廠內所有發電機運轉狀況及訊息整合，電量調度會出現『追逐現象』，輕微時出現電力品質(電壓忽高忽低、頻率變動大，影響用戶電器容易燒毀)不穩，嚴重時甚至全廠停機。

- IMM需提供引擎、發電機、變壓器、高壓開關等重要設備之檢驗合格測試報告。

- MBH發電機組加到舊系統之電氣回路，距離太近容易發生閃絡(Flash over)問題。

- 消防設備及管線目前尚未完成，照理應該無法取得運轉執照，不能運轉，可能STEE極需發電供應查京，該期間所衍生之安全問題不得不注意。

- 安全連鎖故障應該禁止運轉(for example, mist detector failure now , but engine is still running)

4.機組安裝缺失及改善建議測試

- 柴油管內含冷凝水，油霧偵測器誤動作，引擎無法啟動，檢查很久仍未修妥目前暫時Bypass運轉(已檢查過設備安全無虞，且現場有MBH技師負責)。

- 第一次運轉後因為振動之關係，原先配置之管線(水管、滑油管、柴油管、空氣管)和儀器(PT、PS、TS、TT)好像在跳舞一樣，柴油管線到處在洩油，甚至還有螺絲因而鬆動掉下來，所以運轉約半天就停機重新增加support固定。

- Local Control Panel無法顯示轉速、controller無法正常控制轉速(Idle、ramp of starting speed、over speed及相關PID參數)，因為送電前沒有做回路測試，甚至有些線該接而沒接或不該接而接，fuse燒斷好幾支也花了很多時間，更絕得是IMM一支電流勾表因使用歐姆檔量電壓而爆掉(人員無損傷)，我將帶來之勾表暫借IMM使用。

- Engine controller尚未設定好所以啟動時經常發生問題(無法啟動、啟動後就衝到高轉速…)，有時候還要一個人協助調整燃料油量或按Emergency Shutdown，speed sensor只有一只。

- 部分壓力傳送器tube堵塞。

- Turbo Charger滑油、溫度回路檢查。

附圖一 三台MBH發電機組完工運轉

附圖二 高壓線路相間距離改善

三、心得與建議事項

對於此行，我方人員期望機組安裝測試標準所做之努力，STEE總經理及查國相關人員非常感謝我方提出高標準的驗收程序，甚至更希望我方越嚴格越好。除了三部柴油發電機組順利完工運轉外，另提操作維護建議供查國電力公司參考如下：

Comments and Suggestion for operation

- It’s the operators’ duty to carry out the checks listed below, the expenses in time and costs is low compared to that incurred for remedying or that was not recognized in time.

(1). Regular checks (every hour/daily)

- Visual and audible assessment of the system.

- Checking the performance and consumption data

- Checking the most essential engine operating data and ambient conditions.

- Checking the engine, turbocharger, and generator for smooth running.

- Checking system components for tightness (visually).

(2). Periodic checks (daily/every week)

- Evaluate the number of starting events.

- Evaluate the stability of the generator and control linkage.

- Check the engine system for unusual vibrations and extra ordinary noise.

- Check all the system, units, and main components for proper performance.

(3). Fuel Oil system

- Never run the service tank completely empty.

- Regularly drain or exhaust water and slage from the service tank.

- Clean the filters and separators at regular intervals.

(4). Lube oil system

- Check the lube oil level in the service tank and fill up if necessary.

- Check the water content of the lube oil at the specified intervals.

- Clean the filters separators at regular intervals.

(5). Cooling water system

- Check the cooling water level in the expansion tank.

- Check the cooling water outlet temperatures, should the temperature rise above the specified maximum, reduce the engine load and take the remedial measures.

- Check the concentration of the corrosion inhibitor.

(6). Operating values

- The cylinders should be load as evenly as possible. This can be verified by comparison of the ignition pressures and the control linkage position of the injection pumps.

- The exhaust gas temperature have to be checked and compared with the previous measured temperature (acceptance certificate)

- The smoke colour of the exhaust gas is to be checked: oil in the combustion chamber will give a bluish colour, poor combustion or overloading will give the exhaust gases a darker or blacker colour.

(7). Running gear bearing

The MBH engines are not equipped with a bearing temperature monitoring system, thus the oil mist detector is the last chance to monitor the oil vapour which creating by high bearing temperature, or in case of incipient piston failure. It’s the operator’s duty to check and make sure the oil mist detectors are functioning correctly.

- Comments and Suggestion for contract

(1). If there are new project of STEE in the future, those items listed below should better be enclosed in the contract:

- Quality control program for piping, welding, …etc.

- Commissioning program for unit equipment and system.

- The bidding company should instruct STEE’s technicians in the class about mechanical and electrical major items at least 8 hours (for example).

(2). During the period of installation, the bidding company should submit those items listed below:

- Material (piping, welding… etc) examination records.

- Installation reports (daily/monthly)

- Commissioning records (Unit Equipment/system).

- Piping flushing records.

- Lube oil analysis records

(3). In the benefit of STEE, it’s suggested to ask the bidding company to accomplish the items listed below before acceptance:

- Safety protection test for engine and generator.

- Performance test

- Monitoring test.

- Trip test (include over speed, low pressure, high temperature, oil mist detector, … etc)

- Full load test (continuously 72 Hours, 96 Hr, according to STEE’s demand)

- Comments and Suggestion for execution of contract

(1). During the period of contract execution, STEE should organize a commissioning team include the members of STEE, bidding company, to control the schedule and technical details. There should be a leader in the team to distribute work to hold meetings and to overlay the whole project.

(2). It’s also the commissioning team’s duty to establish essential quality control documents. The amounts of document depends on regulars listed below:

- To make records for critical subjects, such as key point of installation, welding, piping, … etc.

- Too much record may cost unexpected manpower, it’s why that commissioning team is so important to make decision what kind of document is necessary, and is not.

(3). Basically, safety regulation should be made by the commissioning team, to remind everyone the dangerous factors, such as falling from high place, electrical shocking, … etc.

(4). To minimize the engine break down, STEE should sent experienced technicians to supervise the proceeding, not only to realize every details of the work, but also they