| GENERAL |
| --- |
| TYPE OF VISIT:  INITIAL INSP. IN-PROCESS INSP. ( FINAL INSP.  OTHER : |
| PURCHASE ORDER NO.： 04P9001 | REQUISITION NO.：ND1.01A |
| GOODS NAME：GENERATOR |
| VENDOR：安葆國際有限公司 | SUB-SUPPLIER： |
| LOCATION：7 Jurong Pier Road, Singapore 619156 | LOCATION： |
| CONTACT：陳志復 先生 | CONTACT： |
| TEL/FAX/MOBILE： 2218-9701 / 22186739 | TEL/FAX/MOBILE： |
| E-MAIL：alice@ampower.com.tw | E-MAIL： |
| PROGRESS |
| ENGINEERING： 100 % | ENGINEERING： (% completed) |
| MATERIAL：: 100 % | MATERIAL： (% received) |
| FABRICATION： 100 % | FABRICATION： (% completed) |
| SCHEDULED COMPLETION DATE：Delivered to site by 2/2/07 | SCHEDULED COMPLETION DATE： |
| PO DELIVERY DATE/SCHEDULE DELIVERY DATE：Delivered to site by 1/5/07 | PO DELIVERY DATE/SCHEDULE DELIVERY DATE： |
| SUMMARY |
| DATE(S) OF THIS VISIT：First time 12/15/06~12/21/06， Second time 1/18/07~1/23/07 | INSPECTION RESULT CONCLUSION: ACCEPTANCE (ACCEPTANCE BY CONDITION REASON: The remaining work shall be completed and factory test report shall be provided before delivery ON HOLD REASON: ＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿ REJECT REASON :＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿＿ |
| NEXT SCHEDULED VISIT： |  |
| COMMENTS ON SCHEDLUE OF DELIVERY: The delivery schedule need to further confirm with construction team. |  |
| 1.REFERENCE DRAWINGS/SPECIFICATIONS: (Include revision nos.) REQUISITION NO.：ND1.01A |

| INSPECTOR’S SIGNATURE：高東閔 | DATE： 12/15/06~12/21/06 & 01/18/07~01/23/07 |
| --- | --- |
| E/M QC MANAGER SIGNATURE： | DATE： |
| THIS MATERIAL CANNOT BE RELEASED/PROCESSED FURTHER WIHOUT WRITTEN AUTHORIZATION FROM CTCI. |

| INSPECTION ACTIVITIES |
| --- |
| 2. INSPECTION ACTIVITIES IDENTIFICATION (Place a mark in each of the boxes below that corresponds with an inspection activity verified or performed. Each activity marked must be fully explained below at section (4) “Inspection Details.”) |
| GENERAL |
| 1.( Material identification and traceability 2.( Appearance and Visual inspection (External) 3. Visual inspection of weld joint fit up / Back gouge preparations 4. Visual insp. of completed welds for detection of effects/discontinuities 5. Specifications 6. Accessories 7.( Full dimensional inspection for compliance with design drawings 8.( Cleaning / Sandblasting / Painting 9. Verification of Material Certificate | 10.( Marking and Identification (name plate data, tags, etc.) 11.( Internal inspection 12.( Vendor data review (CMTR, test records, data sheets, QC records) 13. Review of Welding Procedure Spec. and Procedure Qualification Record 14. Review of Welder/Welding Operator Qualification Records 15. Review of radiographs 16. Check Equipment/Gauge Calibration and Current Calibration Certificate 17. Others: Pre Inspection Meeting and expediting |
| MECHANICAL |
| 16. Mechanical testing (charpy impact, tensile, guided bends) 17. NDE test reports 18. Hardness test : HV  HB  HRC  19. Verification of specified post weld heat treatment 20. Control of welding consumables (filler metals, rods, wire, etc.) 21. In-process welding insp. (adherence to WPS - essential variables) 22. Magnetic particle / Liquid penetrant tests 23. Ultrasonic testing 24. Pressure / Leak test (hydro-static, air, helium, etc.) | 25. Balancing of rotating parts 26.Shaft / Rotor run out 27. Clearance checks 28. Mechanical running tests 29. Over-speed trip test 30. Check of trip systems (low / high oil pressure, vibration, etc) 31. Operational test 32. NPSH test 33. Stroke test 34. Others: |
| ELECTRICITY |
| 35.( Construction inspection 36.( Operation/control test 37.( Insulation resistance test 38. Resistance measurement 39.( Applied voltage test 40. induced voltage test 41. Impulse voltage test 42. Relay function test 43. Short circuit current withstand test 44. Ratio test 45. Polarity and phase relation test | 46. Impedance voltage and load loss test 47. Insulation power factor test 48. Regulation and efficiency test 49. Winding voltage insulation test 50. Locked load test 51.( Capacity test 52. Capacitor's loss test 53. Enclose test 54. Discharging test 55. Uninterruptable test 56. EMC test 57. Others: |
| PERFORMANCE |
| 58.( No Load test 59.( Load test 60. Temperature rise test 61. Vibration test 62.( Audible sound test (Noise test) | 63. Performance test after installed on site 64. Calibration test 65. Operational test 66. Seat leakage test 67. Set pressure test 68. Others |
| 3. DETAILS OF NONCONFORMANCE |
| TYPE OF NONCONFORMITY: Material Workmanship Welding (Fabrication Shipped without Inspection NDE Code violation Dimensional Test Failure Other _____________________________ _____________ | AFFECTED MATERIAL COMPONENT: |
| DESCRIPTION OF NONCONFORMANCE： (Attach sketch and/or continuation page if needed) (Should incl. Initiator, Date, Location) （一）12/15/06~12/21/06 Color of Panel is not as specified. Ampower will re-Spray to per Specified. Customer will supply color sample. Customer request Modbus RS485 Address Mapping Required a cut-out of 300 x 400 mm at the bottom of the panel a per drawing To provide System Ok indication light The factory inspection between the date of 15th to 21 St. December exclude all test on the Generator and its accessories Ampower to reschedule the arrival and inspection date of the Generator due to the reschedule of the shipment date of the generator （二）1/18/07~1/23/07 Customer requested that a NamePlate be fitted to the panel. It was agreed that the nameplate will be fitted on site. Customer requested that an operation Manual to be submitted for the HMI. Ampower agrees to submit this manual Customer request Modbus RS485 Address Mapping. Ampowe will submit this mapping by end Feburary. |
| CORRECTIVE ACTION RECOMMENDATION |
| SUPPLIER’S PROPOSAL TO RECTIFY NONCONFORMANCE： | ACTION TO BE COMPLETED BY: |
| （一）12/15/06~12/21/06 For above item 1、2、3、4、6 Ampower follows to revise and submit related datas （二）1/18/07~1/23/07 For above item 1、2、3 Ampower follows to revise and submit related datas |
| INSPECTOR SUGGESTIONS： （一）12/15/06~12/21/06 Ampower needs to finish all the above comments before delivery of generator （二）1/18/07~1/23/07 Ampower needs to finish all the above comments before delivery of generator |
| CTCI DISPOSITION |
| Correct as per supplier’s proposal Reject Replace Other (See remarks) | REMARKS: |
| E/M QC MANAGER SIGNATURE： | DATE： |
| LEAD ENGINEER SIGNATURE： | DATE： |
| PROJECT QUALITY MANAGER SIGNATURE： | DATE： |
| 4. INSPECTION ACTIVITIES: (Provide complete details of activities performed and tests witnessed as per section (1) above including any activities/inspections that are not listed. Use continuation pages as necessary) 外觀檢查。 器材核對。。 絕緣試驗。 耐壓試驗。 功能測試項目及記錄詳會試記錄表。 12/15/2006 至 12/21/2006搖控盤廠測報告詳附件（一） 1/18/2007 至 1/23/2007搖控盤廠測報告詳附件（二） 1/18/2007 至 1/23/2007發電機廠測報告詳附件（三）、（四）、（五） 搖控盤詳細圖參考附件（六） 發電機詳細圖參考附件（七） |
| 5. INSPECTION PHOTOS REPORT: (Provide complete photos of activities performed and tests witnessed. Use continuation pages as necessary) 廠測日期 12/15/2006~12/21/2006 控制盤外觀檢視(一) 控制盤外觀檢視(二) 內部結線檢視（一） 內部結線檢視（二） 內部結線檢視（三） 內部結線檢視（四） 內部結線檢視（五） 器具檢視（一） 器具檢視（二） 器具檢視（三） 器具檢視（四） 器具檢視（五） |
| 器具檢視（六） 器具檢視（七） 器具檢視（八） 器具檢視（九） 器具檢視（十） 器具檢視（十一） 器具功能測試（一） 器具功能測試（二） 器具功能測試（三） 器具功能測試（四） 參訪KOHLER工廠 |
| 廠測日期 1/18/2007~1/23/2007 （一） 外型檢視(發電機型號確認LSA54L84P) 外型檢視(引擎型號確認20V4000) 發電機啟動馬達 發電機濾油器 發電機排氣管接口 發電機冷卻水過濾器 冷卻風扇 發電機控制盤 引擎控制箱 引擎本体 負載運轉測試 50%負載運轉測試 |
| 廠測日期 1/18/2007~1/23/2007 （二） 100%負載運轉測試 負載變化，電壓/頻率暫態測試（一） 負載變化，電壓/頻率暫態測試（二） 負載變化，電壓/頻率暫態測試（三） 噪音測試（一） 噪音測試（二） 冷卻水異常功能測試 內部接線檢視 發電機測試機台 |