出國報告（出國類別：其它）

「增設金門機場24跑道LDA設備」

工 廠 測 試

出國報告書

服務機關：民用航空局飛航服務總臺

姓名職稱：王桂雄工務員

程正祥工務員

派赴國家：美國堪薩斯

出國期間：98.09.12 ~98.09.23

報告日期：98.10.20

目      次

標題                                                             頁次

壹、目的……………………………………………………………………………………………  2

貳、廠測與會人員…………………………………………………………………………………  3

參、過程………………………………………………………………………………………… 4

肆、廠測內容……………………………………………………………………………………  7

伍、心得及建議…………………………………………………………………………………  12

陸、附錄……………………………………………………………………………………………13

# 壹、目的

本次廠測之主要目的在於測試「增設金門機場24跑道LDA設備」及「汰換花蓮機場03跑道MLS為ILS/DME設備」等2購案所採購之左右定位臺、滑降臺及測距儀等設備是否符合本總臺之合約規範，藉以確保本總臺所購各設備之品質與性能。

金門機場24跑道因地形限制關係，無法設立標準ILS設備，因而24跑道目前僅能使用NDB/DME進場程序（能見度須達3,200公尺以上），嚴重限制24跑道服務容量與品質，為克服地形限制， 故於金門機場24跑道偏架左右定位臺乙座，藉以提供與24跑道夾15度角之進場航道訊號，以避開太武山及石山等主要障礙。預計架設完成後C類航機之能見度標準將可降為2,400公尺，有效降低金門機場24跑道能見度標準，提高飛航服務品質。

花蓮機場03跑道微波降落系統(MLS)使用已逾十餘年，後勤支援不易，且國內各航空公司之機隊早已不再配置MLS機載接收器，使用率偏低，因此各航機降落花蓮機場時，目前僅能實施非精確儀器進場（VOR/DME）程序，為有效改善航機之降落標準，增強花蓮機場飛行安全考量，爰規劃以ILS/DME取代不合時宜之MLS設備。預計花蓮機場增設ILS/DME設備後，航機降落之能見度標準將由現行之3,200公尺，大幅縮減為1,600公尺，改善幅度達50%。

在本次工廠測試過程中，本總臺廠測人員藉由原廠各項儀表與工程師之協助，針對各項設備之性能詳加量測與檢驗，在經由雙方所認可的測試步驟，在合約規範下逐一檢視每個測試的結果並做紀錄，依據測試的結果，做好設備運送前之品質把關工作，避免事後的修改，對維護人員造成困擾，以降低採購風險，確保本採購案依合約規定成功執行。

# 貳、廠測與會人員

總臺代表：

王桂雄  飛航服務總臺/臺北裝修區臺臺北助航設備臺/工務員

程正祥  飛航服務總臺/臺東裝修區臺花蓮助航臺/工務員

SELEX公司代表：

Luke Jones/ Director of Quality

Kurt Rieke/ Navid Product Manager

Douglas Hiles/ NAVAIDS Engineer

參、過程

（一）行程

本次廠測，本總臺選派2名人員前往美國堪薩斯執行工廠測試工作。

本次廠測係假設備原製造廠SELEX Sistemi Integrati公司之#1測試廠房（FAT Room 1）舉行，測試期程共計8日(註：如含行程及星期例假日共計12天)，相關行程如后：

1.98年9月12日搭乘長榮航空班機，由臺北經美國洛杉磯、芝加哥轉機，於9月13日飛抵堪薩斯。

2.98年9月14日至9月18日：進行為期5天之工廠測試。

3.98年9月19日及20日：星期例假日，進行廠測資料整理。

4.98年9月21日：上午09：30~11：30，完成所有測試，由雙方代表於總結會議簽署本次廠測紀錄。

5.98年 9月21日：搭乘長榮航空班機，由美國堪薩斯起飛經達拉斯、洛杉磯轉機，於9月23日返抵臺北。

## （二）　會議議程

Monday 9/14/09

-09:00AM ~ 09:30AM	Opening Meeting – Introduction of Participants

-09:30AM ~ 10:00AM	Factory Tour

-10:00AM ~ 05:00PM	Hualien Localizer System Testing

-05:00PM	End of 1st Day of FAT

Tuesday 9/15/09

-09:00AM ~ 12:00PM	Continue Hualien Localizer System Testing

-01:00PM ~ 05:00PM	Start Hualien Glide Path System Testing

-05:00PM	End of 2nd Day of FAT

Wednesday 9/16/09

-09:00AM ~ 05:00PM	Continue Hualien Glide Path System Testing

-05:00PM	End of 3rd Day of FAT

Thursday 9/17/09

-09:00AM ~ 12:00PM	Start Kinmen Localizer System Testing

-01:00PM ~ 05:00PM	Continue Kinmen Localizer System Testing

-05:00PM	End of 4th Day of FAT

Friday 9/18/09

-09:00AM ~ 05:00PM	Start Hualien DME System Testing

-05:00PM	End of 5th Day of FAT

Monday 9/21/09

-09:30AM ~ 10:30AM	Preparation – Signing of FAT Documentation

-10:30AM ~ 11:30PM	Closing and Open Issues Meeting

# 肆、廠測內容

本次工廠測試於98年9月14日至9月21日由本總臺派員會同承包商SELEX Sistemi Integrati Inc.公司人員於美國堪薩斯工廠進行，本次採購項目包含花蓮機場一套ILS(LLZ/GS/DME)及金門一套LDA(LLZ)，於測試過程中將測試結果逐項紀錄。

測試項目：

一、ILS/LLZ(含金門LDA　LLZ機型：2100)：

TRANSMITTER TESTS

Power Supply Voltages

Transmitter RF Control

Radio Frequency & RF Frequency Control

CRS CSB Power Range

CRS CSB Reflected Power & VSWR

CRS SBO Reflected Power & VSWR

CLR CSB Power Range

CLR CSB Reflected Power & VSWR

CLR SBO Reflected Power & VSWR

RF Power Metering

CRS System Spurious Emissions

CLR System Spurious Emission

CRS Carrier Signal @ Sideband Output

CLR Carrier Signal @ Sideband Output

LO Outputs

CRS Modulation Balance Adjustment

CRS Nav Tones Audio Frequency

CLR Nav Tones Audio Frequency

Identification Signal & Modulation Range

DME Keying Output

MONITOR & CONTROL TESTS

Integral Monitor Voting Logic

Integral, Standby, and Near Field Monitor Alarms

Integral Monitor Reverse Sensing Alarms

Standby Monitor Reverse Sensing Alarms

Antenna Fault Alarms

Monitor Certification & Certification Limits

Transmitter Selection & Indications

System Indications and Controls

Power Supply Functions

Station Transfer Action: Main-to-Standby; Hot Standby Operation

Station Transfer Action: Main-to-Off (Standby Inoperative); Hot Standby Operation .

Station Transfer Action: Main-to-Standby; Cold Standby Operation

Station Transfer Action: Main-to-Shutdown; Cold Standby Operation

Primary & Standby Power

Maintenance Alerts

Station Environmental Accessories

Electronic Controls

Non-Volatility

詳細測試報告，請參閱附錄：花蓮、金門LLZ測試報告

二、ILS/GS(花蓮　機型：2110)：

TRANSMITTER TESTS

Power Supply Voltages

Transmitter RF Control

Radio Frequency & RF Frequency Control

CRS CSB Reflected Power & VSWR

CRS SBO Reflected Power & VSWR

CLR Reflected Power & VSWR

RF Power Metering

CRS CSB/SBO Output-Cable Phase

CRS SYSTEM SPURIOUS EMISSIONS

CLR System Spurious Emission

CRS Carrier Signal @ Sideband Output

LO Outputs

CRS Modulation Balance Adjustment

CRS Nav Tones Audio Frequency

CLR Nav Tones Audio Frequency

MONITOR & CONTROL TESTS

Integral Monitor Voting Logic

Integral, Standby, Monitor Alarms

Integral Monitor Reverse Sensing Alarms

Standby Monitor Reverse Sensing Alarms

Monitor Certification & Certification Limits

Transmitter Selection & Indications

System Indications and Controls

Power Supply Functions

Station Transfer Action: Main-to-Standby; Hot Standby Operation

Station Transfer Action: Main-to-Off (Standby Inoperative); Hot Standby Operation

Station Transfer Action: Main-to-Standby; Cold Standby Operation

Station Transfer Action: Main-to-Shutdown; Cold Standby Operation

Primary & Standby Power

Maintenance Alerts

Station Environmental Accessories

Electronic Controls

Non-Volatility

Modem Control Capability

詳細測試報告，請參閱附錄：花蓮G/S測試報告

三、DME(花蓮　機型：1118A)：

Setup for Frequency Verification Test

Frequency Verifications

Setup for Transmitter Power Output Test

Transmitter Power Output

Setup for Spectral Characteristics Test

Spectral Characteristics

PMDT Setup

General Monitor Configuration Verification

Monitor Alarm Limits Configuration Verification

Monitor Alarm Limit Verification

Monitor Interrogator Signal Generator Tests

Transponder Signal Test

Transponder Decoder Tests

RSCU Controls

Modem Remote Monitoring

Battery Backup

Fault Isolation

Configuration at time of Final Testing

Part Number and Serial Number Documentation

詳細測試報告，請參閱附錄：花蓮DME測試報告

# 心得與建議

  - 「工欲善其事，必先利其器」，此次工廠測試過程中，發現原廠測試的儀器齊全完備，且使用中之儀器均定期後送校驗，以維儀器之精確，相對的維護人員對儀器操作的熟練度愈高，對裝備維護及故障排除將有莫大的助益。所以儀器的操作訓練應加以重視，除一般助導航設備的在職訓練課程外，建議在不影響線上裝備的工作情況下，無論是單獨開課或併隨設備課程，都應加強儀器實際操作訓練。

  - 此次之工廠測試之程序步驟，其實即為設備原始調校的過程，也就是說若能熟悉瞭解廠測的步驟，對於日後設備故障之排除及修復，均有莫大的助益。建議能多派員參與工廠測試，瞭解調校測試及故障排除的過程，亦為日後維護工作，非常重要的一環。

  - 廠測的環境相當於一個實驗室，若能成立一個類似的檢修環境，對於航電人員的在職訓練會有相當的幫助。航電設備一般在上線後因為廿四小時工作，均無法實際做調校測試，除非設備故障停工。但此時卻因為修復的急迫性亦無法長時間做檢測，若能有一相當的模擬設備能隨意拆裝調測，且定期辦理在職複訓，相信對航電人員的技術能力必定會有所提昇。

  - 航電人員於維護裝備時，經常遇到相同設備卻由不同廠商得標，不僅設備的設計理念不同而且零組件也無法互相調用，使得航電人員需要學習多種裝備且不同廠商的硬體維修與軟體應用，備用零組件也常無法發揮互相支援的最大功效，所幸近期在航電技術室的努力下，多件標案合併採購，終於解決了這些困擾的問題，減少了許多訓練及備用零組件經費的支出。

陸、附錄：工廠測試結果